{"text_format":"3","workbook":"xlsx","n_sheets":3,"sheets":["V1","V2","V3"],"read":"whole","date_system":"1900"}

{"sheet":"V1","index":0,"n_rows":28,"n_cols":9,"rows_kept":28}
["Zustandsmatrix Salimax"]
[]
[null,"DEPRECATED"]
["Nr.","Inverter","K3","K2","K1","Erwünscht/Unerwünscht","Kritisch/Unkritisch","Möglich/Unmöglich","Bemerkung"]
[1,"Off/Error","auf","auf","auf","Erwünscht","Unkritisch","Möglich","Aus (IBN Schwarzstart)"]
[2,"Off/Error","auf","auf","zu","Erwünscht","Unkritisch","Möglich","Aus (IBN Standard)"]
[3,"Off/Error","auf","zu","auf","Unerwünscht","Unkritisch","Möglich","Fehlerfall -> Schütz verklebt (K2, Inseltrenn-Schütz)"]
[4,"Off/Error","auf","zu","zu","Erlaubt","Unkritisch","Unmöglich"]
[5,"Off/Error","zu","auf","auf","Unerwünscht","Unkritisch","Unmöglich","Fehlerfall -> Schütz verklebt (K3, AC3025-Schütz)"]
[6,"Off/Error","zu","auf","zu","Unerwünscht","Unkritisch","Unmöglich","Fehlerfall -> Schütz verklebt (K3, AC3025-Schütz)"]
[7,"Off/Error","zu","zu","auf","Unerwünscht","Unkritisch","Unmöglich","Fehlerfall -> Schütz verklebt (K3, AC3025-Schütz)"]
[8,"Off/Error","zu","zu","zu","Unerwünscht","Unkritisch","Unmöglich","Fehlerfall -> Schütz verklebt (K3, AC3025-Schütz)"]
[9,"Netzparallel","auf","auf","auf",null,"Unkritisch","Möglich"]
[10,"Netzparallel","auf","auf","zu",null,"Unkritisch"]
[11,"Netzparallel","auf","zu","auf",null,"Unkritisch"]
[12,"Netzparallel","auf","zu","zu",null,"Unkritisch"]
[13,"Netzparallel","zu","auf","auf","Unerwünscht","Unkritisch",null,"Fehlerfall?!"]
[14,"Netzparallel","zu","auf","zu","Unerwünscht","Unkritisch",null,"Fehlerfall?!"]
[15,"Netzparallel","zu","zu","auf","Unerwünscht","Unkritisch"]
[16,"Netzparallel","zu","zu","zu","Erwünscht","Unkritisch","Möglich","Normalzustand Netzparallelbetrieb"]
[17,"Insel","auf","auf","auf","Erwünscht","Unkritisch","Möglich"]
[18,"Insel","auf","auf","zu",null,"Unkritisch","Möglich"]
[19,"Insel","auf","zu","auf","Unerwünscht","?","Möglich"]
[20,"Insel","auf","zu","zu","Unerwünscht","Kritisch","Möglich","? Fehlerfall -> Schütz verklebt (K2, Inseltrenn-Schütz)"]
[21,"Insel","zu","auf","auf","Erwünscht","Unkritisch","Möglich","Normalzustand Inselbetrieb"]
[22,"Insel","zu","auf","zu","Erwünscht","? Kritisch","Möglich","Netzrückkehr"]
[23,"Insel","zu","zu","auf","Unerwünscht","? Kritisch"]
[24,"Insel","zu","zu","zu","Unerwünscht","Kritisch",null,"Supergau"]

{"sheet":"V2","index":1,"n_rows":28,"n_cols":9,"rows_kept":28}
["Zustandsmatrix Salimax"]
[]
[null,"DEPRECATED"]
["Nr.","Inverter","K1","K2","K3","Erwünscht/Unerwünscht","Kritisch/Unkritisch","Möglich/Unmöglich","Bemerkung"]
[1,"Off/Error","Open","Open","Open","Erwünscht","Unkritisch","Möglich","Aus (IBN Schwarzstart)"]
[2,"Off/Error","Close","Open","Open","Erwünscht","Unkritisch","Möglich","Aus (IBN Standard)"]
[3,"Off/Error","Open","Close","Open","Unerwünscht","Unkritisch","Möglich","Fehlerfall -> Schütz verklebt (K2, Inseltrennschütz)"]
[4,"Off/Error","Close","Close","Open","Erlaubt","Unkritisch","Unmöglich"]
[5,"Off/Error","Open","Open","Close","Unerwünscht","Unkritisch","Unmöglich","Fehlerfall -> Schütz verklebt (K3, AC3025-Schütz)"]
[6,"Off/Error","Close","Open","Close","Unerwünscht","Unkritisch","Unmöglich","Fehlerfall -> Schütz verklebt (K3, AC3025-Schütz)"]
[7,"Off/Error","Open","Close","Close","Unerwünscht","Unkritisch","Unmöglich","Fehlerfall -> Schütz verklebt (K3, AC3025-Schütz)"]
[8,"Off/Error","Close","Close","Close","Unerwünscht","Unkritisch","Unmöglich","Fehlerfall -> Schütz verklebt (K3, AC3025-Schütz)"]
[9,"grid-tied 400V / 50Hz","Open","Open","Open",null,"Unkritisch","Möglich"]
[10,"grid-tied 400V / 50Hz","Close","Open","Open",null,"Unkritisch"]
[11,"grid-tied 400V / 50Hz","Open","Close","Open",null,"Unkritisch"]
[12,"grid-tied 400V / 50Hz","Close","Close","Open",null,"Unkritisch"]
[13,"grid-tied 400V / 50Hz","Open","Open","Close","Unerwünscht","Unkritisch",null,"Fehlerfall?!"]
[14,"grid-tied 400V / 50Hz","Close","Open","Close","Unerwünscht","Unkritisch",null,"Fehlerfall -> Inseltrennschütz hat nicht geschlossen (K2)"]
[15,"grid-tied 400V / 50Hz","Open","Close","Close","Unerwünscht","Unkritisch"]
[16,"grid-tied 400V / 50Hz","Close","Close","Close","Erwünscht","Unkritisch","Möglich","NormalClosestand grid-tied 400V / 50Hzbetrieb"]
[17,"Island 400V / 50Hz","Open","Open","Open","Erwünscht","Unkritisch","Möglich"]
[18,"Island 400V / 50Hz","Close","Open","Open",null,"Unkritisch","Möglich"]
[19,"Island 400V / 50Hz","Open","Close","Open","Unerwünscht",null,"Möglich"]
[20,"Island 400V / 50Hz","Close","Close","Open","Unerwünscht","Kritisch","Möglich","? Fehlerfall -> Schütz verklebt (K2, Island 400V / 50Hztrenn-Schütz)"]
[21,"Island 400V / 50Hz","Open","Open","Close","Erwünscht","Unkritisch","Möglich","NormalClosestand Island 400V / 50Hzbetrieb"]
[22,"Island 400V / 50Hz","Close","Open","Close","Erwünscht",null,"Möglich","Netzrückkehr"]
[23,"Island 400V / 50Hz","Open","Close","Close","Unerwünscht"]
[24,"Island 400V / 50Hz","Close","Close","Close","Unerwünscht","Kritisch",null,"Supergau"]

{"sheet":"V3","index":2,"n_rows":37,"n_cols":9,"rows_kept":37}
["Zustandsmatrix Salimax"]
[]
[null,16,8,4,2,1]
[{"$nulls":3},"Inverters are connected to island bus","Island bus is connected to grid bus","Grid bus is connected to grid"]
["Nr.","Inverter state","Grid mode","K3","K2","K1",null,"Dangerous?","Bemerkung"]
[0,"Off","grid-tied ","Open","Open","Open",null,"Unkritisch","Aus (IBN Schwarzstart)"]
[1,"Off","grid-tied ","Open","Open","Closed",null,"Unkritisch","Aus (IBN Standard)"]
[2,"Off","grid-tied ","Open","Closed","Open",null,"Unkritisch","Fehlerfall -> Schütz verklebt (K2, Inseltrennschütz)"]
[3,"Off","grid-tied ","Open","Closed","Closed",null,"Unkritisch"]
[4,"Off","grid-tied ","Closed","Open","Open",null,"Unkritisch","Fehlerfall -> Schütz verklebt (K3, AC3025-Schütz)"]
[5,"Off","grid-tied ","Closed","Open","Closed",null,"Unkritisch","Fehlerfall -> Schütz verklebt (K3, AC3025-Schütz)"]
[6,"Off","grid-tied ","Closed","Closed","Open",null,"Unkritisch","Fehlerfall -> Schütz verklebt (K3, AC3025-Schütz)"]
[7,"Off","grid-tied ","Closed","Closed","Closed",null,"Unkritisch","Fehlerfall -> Schütz verklebt (K3, AC3025-Schütz)"]
[8,"Off","Island ","Open","Open","Open"]
[9,"Off","Island ","Open","Open","Closed"]
[10,"Off","Island ","Open","Closed","Open"]
[11,"Off","Island ","Open","Closed","Closed"]
[12,"Off","Island ","Closed","Open","Open"]
[13,"Off","Island ","Closed","Open","Closed"]
[14,"Off","Island ","Closed","Closed","Open"]
[15,"Off","Island ","Closed","Closed","Closed"]
[16,"On","grid-tied ","Open","Open","Open",null,"Unkritisch"]
[17,"On","grid-tied ","Open","Open","Closed",null,"Unkritisch"]
[18,"On","grid-tied ","Open","Closed","Open",null,"Unkritisch"]
[19,"On","grid-tied ","Open","Closed","Closed",null,"Unkritisch"]
[20,"On","grid-tied ","Closed","Open","Open",null,"Unkritisch","Fehlerfall?!"]
[21,"On","grid-tied ","Closed","Open","Closed",null,"Unkritisch","Fehlerfall -> Inseltrennschütz hat nicht geschlossen (K2)"]
[22,"On","grid-tied ","Closed","Closed","Open",null,"Unkritisch"]
[23,"On","grid-tied ","Closed","Closed","Closed",null,"Unkritisch","Normalzustand grid-tied betrieb"]
[24,"On","Island ","Open","Open","Open",null,"Unkritisch"]
[25,"On","Island ","Open","Open","Closed",null,"Unkritisch"]
[26,"On","Island ","Open","Closed","Open"]
[27,"On","Island ","Open","Closed","Closed",null,"Kritisch","? Fehlerfall -> Schütz verklebt (K2, Island trenn-Schütz)"]
[28,"On","Island ","Closed","Open","Open",null,"Unkritisch","NormalClosestand Island betrieb"]
[29,"On","Island ","Closed","Open","Closed",null,null,"Netzrückkehr"]
[30,"On","Island ","Closed","Closed","Open"]
[31,"On","Island ","Closed","Closed","Closed",null,"Kritisch","Supergau"]